## Mec. contract
Maintenance Responsibilities
Unit # |  | Type | Location | Make | Model | Serial # | Location | Details | Responsibility of CCI | Responsibility of Contractor | Frequency
AC | 1 | A/C unit | 222 (laboratory) | Ecosaire | CM015G2E000BCGK | 75419BB | 222 (laboratory) | Glycol cooled by drycooler DC-MC (mini-chiller) | Air filter change | Cleaning (evaporator); Mechanical inspection (belts, lubricate, fan wheel check-up, vibration monitoring); Compressor check-up, (leak test, refridgerant charge, operating pressure, operating temperature); Fan motor and compressor current check; Review and adjust alarm set points | Monthly inspection Annual cleaning
AC | 2 | A/C unit | 131 (server room) | Ecosaire | CM030G5EH000BCBK | 75419AA | 131 (server room) | Glycol cooled by drycooler DC-MC (mini-chiller) | Air filter change | Cleaning (evaporator); Mechanical inspection (belts, lubricate, fan wheel check-up, vibration monitoring); Compressor check-up, (leak test, refridgerant charge, operating pressure, operating temperature); Fan motor and compressor current check; Review and adjust alarm set points | Monthly inspection Annual cleaning
AC | 3 | A/C unit | 139 (oven room) | Ecosaire | ECFE41FZ256EHPSKPWX | E2002020045 | 139 (oven room) | Glycol cooled by drycooler DC-AC3 | Air filter change | Cleaning (evaporator); Mechanical inspection (belts, lubricate, fan wheel check-up, vibration monitoring); Compressor check-up, (leak test, refridgerant charge, operating pressure, operating temperature); Fan motor and compressor current check; Review and adjust alarm set points | Monthly inspection Annual cleaning
AHU | 225 | Air Handling Unit | 225 (labarotory) | Circul-aire | MODL'R-100-2H | 751330 | 223 (mechanical room) | Chilled water coil from mini-chiller | Air filter change | Cleaning (evaporator); Mechanical inspection (belts, lubricate, fan wheel check-up, vibration monitoring); Fan motor check; Review and adjust alarm set points | Monthly inspection Annual cleaning
AHU | S1 | Air Handling Unit Hot Heating Water Coil | Laboratory | Sheldons Engineering Ltd | 1H13 H&V | 751888-1 | 219 (fan room) | Indirect gas fired, cooling DX coil, 3 stages R-22 gas | Filter changes and belt regular maintenance; Review and adjust alarm set points | Mechanical inspection (belt, lubricate bearing and motor, fan whell check-up, vibration monitoring); Lubricate and test dampers and actuators Cleaning (coil), operating pressure, operating maintenance and check-up | Monthly inspection Annual cleaning
AHU | S2 | Air Handling Unit Chilling Water Coil Hot Heating Water Coil | Laboratory | Trane | 50MP-HF-TH | 618626 | 220 (fan room) | Indirect gas fired, cooling DX coil, 3 stages R-22 gas | Filter changes and belt regular maintenance; Review and adjust alarm set points | Mechanical inspection (belt, lubricate bearing and motor, fan whell check-up, vibration monitoring); Lubricate and test dampers and actuators Cleaning (coil), operating pressure, operating maintenance and check-up | Monthly inspection Annual cleaning
AHU | S3 | Air Handling Unit Chilling Water Coil Hot Heating Water Coil | Laboratory | Engineered Air | LM-18-C | M10851 S-1 | 221 (fan room) | Indirect gas fired, cooling DX coil, 3 stages R-22 gas | Filter changes and belt regular maintenance; Review and adjust alarm set points | Mechanical inspection (belt, lubricate bearing and motor, fan whell check-up, vibration monitoring); Lubricate and test dampers and actuators Cleaning (coil), operating pressure, operating maintenance and check-up | Monthly inspection Annual cleaning
AHU | S4 | Air Handling Unit | Laboratory | Engineered Air | DG-200-C | M108518-5A | 219 (fan room) | Indirect gas fired, cooling DX coil, 3 stages R-22 gas | Filter changes; Mechanical inspection (belt, lubricate, fan whell check-up, vibration monitoring); Lubricate and test dampers and actuators; Review and adjust alarm set points | Cleaning (evaporator), gas burner; Compressor check-up (leak test, refridgerant charge, operating pressure, operating temperature); Gas burner tune-up and inspection; C-Track panel maintenance and check-up | Monthly inspection Annual cleaning Annual gas burner tune-up
AHU | S5 | Air Handling Unit Chilling Water Coil Hot Heating Water Coil | Laboratory | McQuay | CAH050GDAC | FBOU090301763 | Catwalk | Indirect gas fired, cooling DX coil, 4 stages R-22 gas | Filter changes and belt regular maintenance; Review and adjust alarm set points | Mechanical inspection (belt, lubricate bearing and motor, fan whell check-up, vibration monitoring); Lubricate and test dampers and actuators Cleaning (coil), operating pressure, operating maintenance and check-up | Monthly inspection Annual cleaning
AHU | S6 | Air Handling Unit | Roof | Engineered Air | DG-200-C | M10851 S-5A | Catwalk | Indirect gas fired, cooling DX coil, 4 stages R-22 gas | Filter changes; Mechanical inspection (belt, lubricate, fan whell check-up, vibration monitoring); Lubricate and test dampers and actuators; Review and adjust alarm set points | Cleaning (evaporator), gas burner; Compressor check-up (leak test, refridgerant charge, operating pressure, operating temperature); Gas burner tune-up and inspection; C-Track panel maintenance and check-up | Monthly inspection Annual cleaning Annual gas burner tune-up
BOIL | B1 | Gas | Room 218 | Lochinvar | CHN2071 | E06H00186695 | 218 | Boiler | N/A | Annual combustion test, maintenance according to B149.1 gas code. | Monthly inspection
BOIL | B2 | Gas | Room 218 | Lochinvar | CHN2071 | E06H00186955 | 218 | Boiler | N/A | Annual combustion test, maintenance according to B149.1 gas code. | Monthly inspection
BOIL | B3 | Gas | Room 218 | Lochinvar | CHN2071 | E06H00186694 | 218 | Boiler | N/A | Annual combustion test, maintenance according to B149.1 gas code. | Monthly inspection
BOIL | DB | Gas | Room 218 | BIASI | B40/8 | AS-26.214 | 218 | Domestic Water Boiler | N/A | Annual combustion test, maintenance according to B149.1 gas code. Includes associated pumps. | Monthly inspection
BOIL | BP | Mechnical pump (x3) | Pump | Armstrong | 816032MF-000 | N/A | 218 |  | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | Marathon | DVH-56T17D1076B P | AS- 26.214 | 218
CHL | M1-2 | Mini-Chiler (2 compressors) | Chilled water for AHU-225 room 223 (for lab 225) | MTL, Envirochill | DCTC024WC-1C1S-5 | 2398(99)-04-05 | 219 (fan room) | Glycol cooled by drycooler (DC-MC) | N/A | Compressor check-up (leak test, refridgerant charge, operating pressure, operating temperature); Review and adjust alarm set points; Monthly inspection, temperature , pressure, compressor and heat exchanger | Monthly
CIR | P5 | Circulating pump | Pump | Armstrong | 1.5x1.5x8 4380 | 517954 | Mechanical Room | Vertical In line | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | WEG | TE180X0H | 1022841500
CIR | P6 | Circulating pump | Pump | Armstrong | 1.5x1.5x8 4380 | 517955 | Mechanical Room | Vertical In line | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | Baldor | VJMM31647-4 | 35E622-1111
CU | S4 | Condensing unit S4 | AHU-S4 | Engineered Air | CUB846-0 | B40561 CU-5A | Roof | 6 stages, 8 fans R-22 gas | N/A | Cleaning (condensor); Mechanical inspection (fans check-up, vibration monitoring); Compressor check-up (leak test, refridgerant charge, operating pressure, operating temperature); Fan motor and compressor current check; Review controls and safety settings | Monthly inspection Annual cleaning
CU | S6 | Condensing unit S6 | AHU-S6 | Engineered Air | FWE524/DG180/O | 60948 S-6 | Roof Catwalk | 4-stages, 4 fans R-22 gas | N/A | Cleaning (condensor); Mechanical inspection (fans check-up, vibration monitoring); Compressor check-up (leak test, refridgerant charge, operating pressure, operating temperature); Fan motor and compressor current check; Review controls and safety settings | Monthly inspection Annual cleaning
DC | MC | Drycooler mini-chiller | AC-2 (server room), AC-1 (lab 222), freezer | Ecosaire | FID016-8-F14 | 75419CC | Roof | 2-pumps 1,5 hp, 1-fan 1,5hp | N/A | Cleaning (condenser); Mechanical inspection (fans and pumps check-up, vibration monitoring); Fan motors and pumps current check; Monitoring glycol density and charge pressure; Monitoring air charge of expansion tank; Review controls and safety settings. | Monthly inspection Annual cleaning
DC | AC3 | Drycooler AC-3 | AC-3 Room 139 (oven room) | Ecosaire | DEM70-56E14 | E2002020046 | Roof | 2-pumps 1,5 hp, 3-fans 1/2 hp | N/A | Cleaning (condenser); Mechanical inspection (fans and pumps check-up, vibration monitoring); Fan motors and pumps current check; Monitoring glycol density and charge pressure; Monitoring air charge of expansion tank; Review controls and safety settings. | Monthly inspection Annual cleaning
DSH | 225 | Dehumidifier | AHU-225 for room 225 | BRYAIR | MP175 | 2005E 765T | 225 (laboratory) |  | N/A | Check or replace process and reactivation filters. Check for rotor air leaks. Clean desiccant rotor. | Quaterly filters check and air leaks. Annual cleaning.
HUM | H1 | Humidifier (gas) | S3 | Dri-Steem | GTS04-200 | 1142873-01-01 | 219 (fan room) |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check burner operation; Check the flue piping and connection; Check for gas leaks on piping and valves; Check the ignition system and the blower ramp; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operating set point and sequences from the controller | Monthly inspection Annual cleaning
HUM | H2 | Humidifier (gas) | S2 | Dri-Steem | GTS04-200 | 1142873-02-01 | 219 (fan room) |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check burner operation; Check the flue piping and connection; Check for gas leaks on piping and valves; Check the ignition system and the blower ramp; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operating set point and sequences from the controller | Monthly inspection Annual cleaning
HUM | H3 | Humidifier (gas) | S5 | Dri-Steem | GTS04-600 | 1142873-03-01 | 219A (fan room) |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check burner operation; Check the flue piping and connection; Check for gas leaks on piping and valves; Check the ignition system and the blower ramp; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operating set point and sequences from the controller | Monthly inspection Annual cleaning
HUM | H4 | Humidifier (gas) | S5 | Dri-Steem | GTS04-600 | 1142873-03-02 | 219A (fan room) |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check burner operation; Check the flue piping and connection; Check for gas leaks on piping and valves; Check the ignition system and the blower ramp; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operating set point and sequences from the controller | Monthly inspection Annual cleaning
HUM | H5 | Humidifier (gas) | S4 | Dri-Steem | GTS04-800 | 1142873-05-01 | 219 (fan room) |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check burner operation; Check the flue piping and connection; Check for gas leaks on piping and valves; Check the ignition system and the blower ramp; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operating set point and sequences from the controller | Monthly inspection Annual cleaning
HUM | H6 | Humidifier (gas) | S5 | Dri-Steem | GTS04-800 | 1157601-01-01 | 219 (fan room) |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check burner operation; Check the flue piping and connection; Check for gas leaks on piping and valves; Check the ignition system and the blower ramp; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operating set point and sequences from the controller | Monthly inspection Annual cleaning
HUM | 10 | Humidifier (electric) | S6 | Dri-Steem | VM99-34 | 1149269-01-02 | 228 (laboratory) |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check the electric heater; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operationg set point and sequences from the controller | Monthly inspection Annual cleaning
HUM | 10A | Humidifier (electric) | S6 | Dri-Steem | VM99-34 | 1149269-01-01 | 228 (laboratory) |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check the electric heater; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operationg set point and sequences from the controller | Monthly inspection Annual cleaning
HUM | H11 | Humidifier (electric) | S4 | Dri-Steem | VLC-84-4 | 1144814-05-01-CC | 219 (fan room) |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check the electric heater; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operationg set point and sequences from the controller | Monthly inspection Annual cleaning
HUM | 225 | Humidifier (electric) | AHU-225 for room 225 | Nortec | NHDI-010 | 65627DIB001 | 223 (mechanical room) |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check the electric heater; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operationg set point and sequences from the controller | Monthly inspection Annual cleaning
HUM | S6 | Humidifier (Gas) | S6 | Engineered Air | SH240/O | 60948 S-6A | Roof Catwalk |  | N/A | Test the low level cut-off; Clean the water level probes; Clean the heat exchanger; Test and inspect the water filling valve; Check burner operation; Check the flue piping and connection; Check for gas leaks on piping and valves; Check the ignition system and the blower ramp; Check the steam distribution piping; Test the automatic drain valve; Review and adjust the operating set point and sequences from the controller | Monthly inspection Annual cleaning
MUA | 1 | Make-up air unit | Spray-booth #1 | Global Solutions | 2X10DF-B | 23580405 | 117 (spray-booth) | Direct fire gas | Filter changes; mechanical inspection (belts, lubricate, fan wheel check-up, vibration minotoring); Fan motor current check; Review and adjust alarm et points; Check operating sequences | Gas burner inspection and tune-up | Annual
MUA | 2 | Make-up air unit | Spray-booth #2 (room 135 fine arts, large) | Engineered Air | HE-131-1 | M12224 | Roof | Direct fire gas | Filter change; mechanical inspection (belts, lubriacte, fan wheel check-up, vibration monitoring); Fan motor current check; Review and adjust alarm set points; Check operating sequences | Gas burner inspection and tune-up | Annual
MUA | 3 | Make-up air unit | Spray-booth #3 (room 135 fine arts, small) | AAON Air wise | MN 18 | CN3880 | Roof | Direct fire gas | Filter change; mechanical inspection (belts, lubriacte, fan wheel check-up, vibration monitoring); Fan motor current check; Review and adjust alarm set points; Check operating sequences | Gas burner inspection and tune-up | Annual
RTU | 1 | Roof-Top-Unit | Front Entrance | Lennox | LGA036H2BS2J | 5608B00978 | Roof | 4 stages 4,2A, indirect gas burner | Filter Change | Cleaning (evaporator), gas burner; Compressor check-up (leak test, refridgerant charge, operating pressure, operating temperature); Gas burner tune-up and inspection; Compressor current check; Mechanical inspection (belts, lubricate, fan wheel check-up, vibration monitoring); Fan motor current check; review and adjust alarm and set points | Monthly inspection Annual cleaning Annual gas burner tune-up
VSD | CP5 | Variable speed drive | CP5 | Danfoss | Type 1/ IP21/ IP4X Top |  | Mechanical Room | 59.8 Hz, 56410kWh | N/A | Check and adjust parameters | Annual
VSD | S4 | Variable speed drive | S4 | Danfoss | 174G4880 | 332100Y406 | 219 (fan room) |  | N/A | Check for hot spots with infrared thermometer. Tightnen the connections and clean-up the cabinet. Check and adjust parameters. | Annual
VSD | S5 | Variable speed drive | S5 | OMRON | CIMR-P5M5037 | N2W1495-2-4 | 224A (laboratory) |  | N/A | Check for hot spots with infrared thermometer. Tightnen the connections and clean-up the cabinet. Check and adjust parameters. | Annual
VSD | S6 | Variable speed drive | S6 | ABB | ACH580-01-022A-6 | 2210905966 | 224A (laboratory) |  | N/A | Check for hot spots with infrared thermometer. Tightnen the connections and clean-up the cabinet. Check and adjust parameters. | Annual
| PS2 | Mechnical pump | Pump | Armstrong | 119041-200 | 1817-0132 |  |  | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | Compass | R2075D1-8.5x2 | 119181-113
| PA4 | Mechnical pump | Pump | Armstrong | 1.5D 1060-001 | 715483 | Mechanical Room |  | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | Century | H1048L | 357136M
| PA5 | Mechnical pump | Pump | Armstrong | 1.5D 1060-001 | 715483 | Mechanical Room |  | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | Armstrong | DVH-56T17D1100B | 131042-068
| P5 | Mechnical pump | Pump | Armstrong | 3x1.5x10 4030 | 566695 | Mechanical Room |  | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | Baldor | M3218T-5 | F0702284314
| P6 | Mechnical pump | Pump | Thrush | 2G | 2x2.5x9PF | Mechanical Room |  | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | GE | 1F1215P | BL1028
| P7 | Mechnical pump | Pump | Thrush | 2G | 2x2.5x9PF |  |  | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | WEG | T001C0X0N0000 | 10705364
| P9 | Mechnical pump | Pump | Armstrong | HB0054FJB | 4001322-068 |  |  | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | Armstrong | 2x2x10 4380 | 566784
| P10 | Mechnical pump | Pump | Armstrong | 2x2x8 4380 | 179038 |  |  | Mechanical inspection | Provide spare parts and labor in the event of breakage | If needed
|  |  | Motor | US Electrical Motors | DEF4DP | G50668W0ZM0453
|  | Walk In Freezer |  | Copeland | CF06K6E-TFS-253 | 04B014534 |  |  | Mechanical inspection, clean condenser, annual leak check, verify temperactures. | Provide spare parts and labor in the event of breakage | If needed
Notes :
1) Contract includes all associated equipment, piping, thermal transfer fluid, controls, strainers, valves, bearings and vents.
2) All Air Handling Units (AHUs) shall be pressure washed with water/soap annually ; units S-4, S-6 shall be washed after normal working hours.
3) All Air Handling Units (AHUs) will not be shut down without the permission of CCI site supervisor of operation and maintenance or the supervisor's replacement.
4) Air filter change by CCI Technicians
5) Contract includes annual gas burner inspection for Make-up Air units.
6) It is possible that the boilers may be replaced during the term of this contract. If this situation arises, an ammendment with serial numbers make and model will be made to reflect the updated equipment.