## Aspect # 1
MATSQUI INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 1: Fire alarm system/devices
Device | main alarm panel | annunciator panels | manual pull station | manual pull station-2stage | smoke alarm | smoke detector | smoke detector | heat detector | heat detector RHT | excess pressure | pressure switch | pressure switch | flow switch | Supervisory device | horn | strobe | horn with strobe | bell | end of line resistor
Type | [5 empty] | duct | photo or ion | fixed temp | rate of rise | pump run | low water | low air |  | other
BUILDING | Make/Stage | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty
A15 | 1- GE Edwards EST 3 - 1 stage |  | 3 | [5 empty] | 5 | [5 empty] | 2 |  |  |  | 1
A16 | 1- GE Edwards EST 3 - 1 stage |  | 2 | [5 empty] | 3 | [5 empty] | 1 |  |  |  | 1
A18 | 1- GE Edwards EST 3 - 1 stage |  | 2 | [5 empty] | 5 | [5 empty] | 1 |  |  |  | 1
A20 | 1- GE Edwards EST 3 - 1 stage |  | 3 | [5 empty] | 5 | [6 empty] | 2 |  | 2
A21 | 1- Edwards EST 3 (node 28) - 2 stage | 1 |  | 9 |  | 1 | 8 |  | 1 |  |  |  | 2 |  | 8 |  | 7
M1a | 1- GE Edwards EST 3 - 1 stage |  | 3 |  |  |  | 3 | 4 | 2 | [5 empty] | 2 |  |  |  | 4
M2a,b,c,d and M12 | 1- GE Edwards EST 3 - 2 stage | 4 | 3 | 4 | 3 | 8 | 69 | 2 | 14 |  |  |  | 7 | 15 | 8 | 4 | 1 |  | 8
M2e1/2/3 | 1- GE Edwards EST 3 - 2 stage |  |  | 1 |  | 12 | 22 | [5 empty] | 3 | 7 | 6
M2e4 | 1- GE Edwards EST 3 - 1 stage |  | 3 |  |  | 9 |  |  | 4 | 1 |  |  | 3 | 7 | 3 |  |  |  | 1
M2T1 | 1- GE Edwards EST 3 - 1 stage |  | 2 | [9 empty] | 1 | 3 | 1 |  |  |  | 1
M3 | 1- GE Edwards EST 3 - 2 stage | 2 |  | 3 |  | 9 | 362 |  |  |  | 1 | 1 | 6 | 7 | 19 | 3 | 1 |  | 3
M4 & M5 | 1- GE Edwards EST 3 - 1 stage |  | 11 |  |  | 6 | 5 |  | 1 |  | 1 | 1 | 6 | 14 | 10 |  |  | 1
M5c | 1- GE Edwards EST 3 - 1 stage |  | 3 |  |  | 3 |  | 1 |  |  |  |  | 1 | 5 | 6 |  |  |  | 2
M6 & M7 | 1- Edwards EST 3 - 1 stage |  | 3 |  |  | 1 | [6 empty] | 1 | 5 | 7 | 2 |  |  | 2
M8 | 1- GE Edwards EST 3 - 1 stage |  | 16 |  |  | 1 | 1 |  | 2 |  |  |  | 2 | 9 | 13 | 4
M9 | 1- GE Edwards EST 3 - 1 stage |  | 2 |  |  |  | 1 | [5 empty] | 3 | 6 | 1 |  |  |  | 1
M10 | 1- GE Edwards EST 3 - 1 stage |  | 2 |  |  |  | 1 |  |  |  | 1 |  | 1 | 3 | 1
M13 | 1- GE Edwards EST 3 - 1 stage |  | 2 |  |  |  |  | 2 | 12 | [5 empty] | 1 |  |  |  | 2
M14 | [7 empty] | 1 -combo | [8 empty] | 1
M14A | 1- Edwards EST (node 2) - 1 stage |  | 8 |  |  |  | 9 | 1- combo |  |  |  |  | 4 |  | 9 |  | 1 |  | 3
M14B | [7 empty] | 1- combo | [8 empty] | 2
M15 | 1- Edwards EST (node 2) - 1 stage |  | 8 |  |  |  | 9 |  | 3 |  |  |  | 4 |  | 9 |  |  |  | 3
M16 | 1- Edwards EST 3 (node 25) - 2 stage | 1 |  | 7 |  |  | 124 | [5 empty] | 12 |  |  |  | 28 |  | 3
TOTAL | 20 | 8 | 68 | 24 | 3 | 50 | 605 | 9 | 57 | 1 | 3 | 2 | 52 | 77 | 99 | 15 | 35 | 3 | 33

## Aspect # 2
MATSQUI INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 2: Sprinkler systems/trees
Component | Dry sprinkler system | Wet sprinkler system | water motor gong | sprinkler activation-other device | flow valve (supy) | Fire dept connections
BUILDING | Qty | Qty | Qty | Qty | Qty | Qty
A21 |  | 2 |  |  | 5 | 1
M2a,b,c,d and M12 |  | 7 | 1
M2e1/2/3 |  | 3 |  |  |  | 1
M2e4 |  | 4
M2T1 |  | 1 |  |  |  | 1
M3 | 1 | 1
M4 & M5 | 1 | 5 | 1
M5c |  | 1 |  |  |  | 1
M6 & M7 |  | 1
M8 |  | 2 |  |  |  | 1
M9 |  | 1 |  |  |  | 1
M10 |  | 1 |  |  |  | 1
M14 |  |  |  | 3
M15 |  | 4 |  |  | 6
M16 |  | 12 |  |  | 16
TOTALS | 2 | 45 | 2 | 3 | 27 | 7
Total # of gauges on site for each type of sprinkler system | 2 | 52

## Aspect # 3
MATSQUI INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 3: Emergency Lighting
BUILDING | Location | Make | Watts | # of remote heads
M12 | a&d | Ready-Lite | 150 | 14
M1a | PE | Ready-Lite | 75 | 8
M1a | Electrical room west | Lumacell | 360 | 2
M2a | admin rm 125 | Ready-Lite | 36 | 2
M2a | admin rm 158 | Ready-Lite | 36 | 2
M2a | mccp | Ready-Lite | 36 | 2
M2b | v&c west | Ready-Lite | 36 | 2
M2b | v&c east | Ready-Lite | 36 | 4
M2b | V & C | Ready-Lite | 75 | 2
M2c | security post | Ready-Lite | 36 | 2
M2c | by security post | Ready-Lite | 36 | 2
M2c | by cell 13 | Ready-Lite | 36 | 2
M2c | by cell 20 | Ready-Lite | 36 | 2
M2c | trailer | Ready-Lite | 36 | 4
M2d | closet | Ready-Lite | 150 | 0
M2d | by cell 4 | Ready-Lite | 36 | 2
M2d | by cell 7 | Ready-Lite | 36 | 2
M2d | security post | Ready-Lite | 36 | 2
M2e 123 | reception | Ready-Lite | 36 | 2
M2e 123 | pharmacy | Ready-Lite | 36 | 2
M2e 123 | treatment rm | Ready-Lite | 36 | 2
M3 | 1st floor control | Ready-Lite | 36 | 2
M3 | 1st floor control | Ready-Lite | 36 | 2
M3 | 1st floor control | Ready-Lite | 36 | 2
M3 | 1st floor control | Ready-Lite | 36 | 2
M3 | 2nd floor control | Ready-Lite | 36 | 2
M3 | 2nd floor control | Ready-Lite | 36 | 2
M3 | 2nd floor control | Ready-Lite | 36 | 2
M3 | 2nd floor control | Ready-Lite | 36 | 2
M3 | 2nd floor control | Ready-Lite | 36 | 2
M3 | 3rd floor control | Ready-Lite | 36 | 2
M3 | 3rd floor control | Ready-Lite | 36 | 2
M3 | 3rd floor control | Ready-Lite | 36 | 2
M3 | 3rd floor control | Ready-Lite | 36 | 2
M3 | 3rd floor control | Ready-Lite | 36 | 2
M3 | 3 west | Ready-Lite | 36 | 4
M3 | 3 south | Ready-Lite | 36 | 4
M3 | 3 east | Ready-Lite | 36 | 4
M3 | 3 north | Ready-Lite | 36 | 4
M3 | 2 north | Lumacell | 36 | 4
M3 | 2 east | Ready-Lite | 36 | 4
M3 | 2 south | Ready-Lite | 36 | 4
M3 | 1 west | Ready-Lite | 36 | 4
M3 | 1 south | Ready-Lite | 36 | 4
M3 | 1 east | Ready-Lite | 36 | 4
M3 | 1 north | Ready-Lite | 36 | 4
M3 | 2 west | Ready-Lite | 36 | 4
M3 | Electrical room 3rd floor | Ready-Lite | 100 | 6
M4 | cook chill prod kitchen | Ready-Lite | 36 | 10
M4 | kitchen | Ready-Lite | 36 | 8
M4 | kitchen | Ready-Lite | 36 | 8
M4 | Kitchen by coolers | Lumacell | 36 | 2
M4 | Prod. Kitchen corridor | Lumacell | 360 | 4
M4 | Prod. Kitchen ration room | Lumacell | 360 | 6
M4 | Prod. Kitchen loading bay | Lumacell | 360 | 8
M4 | Prod. Kitchen mixing room | Lumacell | 360 | 6
M5 | gym east | Ready-Lite | 36 | 2
M5 | gym south | Ready-Lite | 36 | 2
M5 | gym south west | Ready-Lite | 36 | 2
M5 | gym north west | Ready-Lite | 75 | 2
M5 | gym west | Ready-Lite | 36 | 2
M5 | gym north east | Ready-Lite | 75 | 2
M5 | billard storage rm | Ready-Lite | 150 | 4
M5 | billard storage | Ready-Lite | 150 | 6
M5b | programs lower | Ready-Lite | 36 | 2
M5b | programs upper | Ready-Lite | 36 | 2
M5b | programs stairs | Ready-Lite | 36 | 2
M5b | Programs upper east | Ready-Lite | 36 | 2
M5c | social d | Ready-Lite | 36 | 2
M5c | hobby shop | Ready-Lite | 36 | 2
M6-M7 | mech rm | Ready-Lite | 36 | 8
M6-M7 | carpentry | Ready-Lite | 36 | 2
M6-M7 | facilities office | Ready-Lite | 36 | 2
M8 | rm 108a | Ready-Lite | 18 | 2
M8 | by rm 111 | Ready-Lite | 18 | 2
M8 | rm 111 | Ready-Lite | 36 | 2
M8 | rm 123 | Ready-Lite | 36 | 2
M8 | rm 109a | Ready-Lite | 120 | 4
M8 | rm 108a | Ready-Lite | 36 | 2
M8 | iss at back | Ready-Lite | 36 | 2
M8 | iss at back | Ready-Lite | 36 | 2
M8 | iss rm 120 | Ready-Lite | 36 | 2
M8 | iss at front | Ready-Lite | 36 | 2
M8 | iss storage | Ready-Lite | 36 | 2
M8 | iss storage | Ready-Lite | 36 | 2
M8 | textiles | Ready-Lite | 36 | 2
M8 | Room 131 west entry | Ready-Lite | 36 | 2
M8 | Room 209 | Ready-Lite | 36 | 2
M12 | a&d | Ready-Lite | 150 | 14
M13 | warden | Ready-Lite | 75 | 5
A15 | corcan storage | Emergi-lite | 360 | 10
A18 | corcan office trailer | Ready-Lite | 150 | 8
A20 | gen bldg north | Emergi-lite | 360 | 2
A20 | gen bldg south | Emergi-lite | 360 | 4
A20 | gen bldg east | Emergi-lite | 360 | 4
A21 | GO bldg | Emergi-lite | 360 | 10
A21 | GO bldg | Emergi-lite | 360 | 6
A21 | GO bldg | Emergi-lite | 360 | 6
A21 | GO bldg | Emergi-lite | 360 | 8
A21 | GO bldg | Emergi-lite | 150 | 4
A21 | GO bldg | Emergi-lite | 360 | 8
Total | 101 |  |  | 363

## Aspect # 4
MATSQUI INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 4: Fire Extinguishers/Exit lights on battery
Type | ABC | K-guard | All exit lights on battery
BUILDING | Qty | Qty | Qty
A15 | 3 |  | 2
A16 | 5
A20 | 4
A21 | 6 |  | 20
M1a | 6
M2a | 10
M2b | 5 |  | 3
M2c | 5
M2T1 |  |  | 2
M2d | 4
M2e1/2/3 | 11
M2e4 | 3
M3 | 7
M4 | 5 | 2 | 4
M5 | 4
M5b | 4 |  | 2
M5c | 8
M6 | 3
M7 | 12
M8 | 35
M9 | 2
M10 | 2 |  | 1
M12 | 3
M13 | 3 |  | 2
M14 | 3
M15 | 10 |  | 10
M16 | 4 |  | 5
MT3 | 1
P1-P7 | 6
P9 | 1
TOTAL | 175 | 2 | 51

## Aspect # 5
MATSQUI INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 5: Fire Hydrants
Equipment | Hydrant only |  | All Hydrants require Dechlorination during flow testing and/or flushing
Location on site | Make | Type | High risk to environment -Dechlorinate
outside west fence M16 (#11) | Brigadier Clow |  | dechlorinate
west corner of M16 (#10) | Brigadier Clow |  | dechlorinate
south end of M16 (#9) | Brigadier Clow |  | dechlorinate
north corner of M3 (#8) | City Iron | TC C71P | dechlorinate
west corner of M3 (#12) | City Iron | TC C71P | dechlorinate
outside west fence of M3 (#21) | Brigadier Clow |  | dechlorinate
north side of M15 (#14) | City Iron | TC C71P | dechlorinate
50 metres west of M13 (#18) | City Iron | TC C71P | dechlorinate
north side of M5 gym (#7) | Century Meuller |  | dechlorinate
south side between M5 and M4 (#15) | City Iron | TC C71P | dechlorinate
north east corner of M2e123 (#6) | City Iron | TC C71P | dechlorinate
south side of M9 (#16) | City Iron | TC C71P | dechlorinate
south side of M2C (#17) | TC Terminal City Iron Works |  | dechlorinate
west side of M2e4 (#5) | Century Meuller |  | dechlorinate
between M2e4 and M8 (#4) | Century Meuller |  | dechlorinate
south east corner of M8 (#3) | City Iron | TC C71P | dechlorinate
north corner of M6 (#1) | City Iron | TC C71P | dechlorinate
south corner of M7 (#2) | City Iron | TC C71P | dechlorinate
east side of A21 (#19) | Brigadier Clow |  | dechlorinate
west side of A16 (#20) | Brigadier Clow |  | dechlorinate
South Side M3 (#13) | Brigadier Clow |  | dechlorinate
East Side A21 (#22) | Brigadier Clow |  | dechlorinate
TOTAL | 22 |  | 22

## Aspect # 6
MATSQUI INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 6: Back Flow Preventers
| Domestic water | Fire | Confined space
BUILDING | Qty | Qty | YES or NO
A21 | 2 | 1 | No
M2a |  | 1 | No
M2c |  | 1 | No
M2e1/2/3 |  | 1 | No
M2e4 |  | 1 | No
M2T1 |  | 1 | No
M4 | 5 | 1 | No
M5b |  | 1 | No
M5c |  | 2 | No
M7 | 1 |  | No
M8 | 1 | 1 | No
M10 |  | 1 | No
M15 | 2 | 1 | No
M16 | 1 | 1 | No
In ground hot box next to domestic water service bldg-king rd. |  | 1 | No
Domestic water service bldg-king rd. | 1 |  | YES
Sewage lift station | 1 |  | No
New Tower | 1 |  | No
TOTAL | 15 | 15

## Aspect # 7
MATSQUI INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 7: Standpipe/Hose Cabinet systems (occupant use hose)
Material,class, type and demand | Canvass | Class-qty of each class of system in each building | Type of standpipe and qty of each type per bldg | Standpipe system design demand | Length of standpipe HOSES
BUILDING | QTY | Class 1, 2 or 3 | eg.automatic/ dry/manual/wet/ semi-automatic dry | GPM - L/min | Length in feet
M6/7 | 1 | 2 | automatic |  | 1 1/2" -100ft each
M2a | 3 | 2 | automatic |  | 1 1/2" -100ft each
M2c | 1 | 2 | automatic |  | 1 1/2" -100ft each
M2e1/2/3 | 4 | 2 | automatic |  | 1 1/2" -100ft each
M2e4 | 2 | 2 | automatic |  | 1 1/2" -100ft each
M3 | 12 | 2 | automatic |  | 1 1/2" -100ft each
M4 | 1 | 2 | automatic |  | 1 1/2" -100ft each
M5 | 1 | 2 | automatic |  | 1 1/2" -100ft each
M5b | 2 | 2 | automatic |  | 1 1/2" -100ft each
M5c | 2 | 2 | automatic |  | 1 1/2" -100ft each
M12 | 1 | 2 | automatic |  | 1 1/2" -100ft each
M16 | 2 | 2 | automatic |  | 1 1/2" -100ft each
TOTAL | 30
Note: all hoses replaced 2015

## Aspect # 8
MATSQUI INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 8: Kitchen Sprinkler Suppression systems
EQUIPMENT | M4 - rm 180 (production kitch steam kettle) | M4 - rm 180 (production kitch cook/chill) | M4 - rm 53 (population kitchen)
Make | Badger |  | Badger
Model | RG6 UCH |  | RG4 GMXV
Actuation type | CO2 Cartridge |  | CO2 Cartridge
Number of cylinders | 1 |  | 3
Number of nozzles | 2 | 2 | 23
Number of suppression system fusible links | 2 | 2 | 0- only heat detecting rods
Size of cylinders | 6 gallon |  | 4 gallon
Fire damper assembly type | none | none | Thermostat - 1
Fire damper assembly fusible links to replace | none | none | none